{"text_format":"3","workbook":"xls","n_sheets":7,"sheets":["표지","주1A동","주2B동","주3C동 ","주5동(1~2라인)","주5동(3~4라인)","주7동"],"not_rendered":{"images":30,"external_links":1,"defined_names":7},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"표지","index":0,"n_rows":13,"n_cols":11,"rows_kept":13,"flags":["formulas_cached_only"]}
{"$rows_empty":12}
[{"$nulls":10},"SITE SURVEY 협의서"]

{"sheet":"주1A동","index":1,"n_rows":77,"n_cols":10,"rows_kept":77,"merged":[[0,0,1,0],[0,1,1,9],[2,0,10,1],[2,2,3,3],[2,4,3,5],[2,6,3,7],[2,8,3,9],[4,2,5,3],[4,4,5,9],[6,2,7,3],[6,4,7,5],[6,6,7,7],[6,8,7,9],[8,2,10,3],[8,4,10,9],[11,0,22,1],[11,2,12,2],[11,3,11,5],[11,6,11,8],[11,9,12,9],[12,3,12,4],[12,6,12,7],[13,2,14,2],[13,3,14,4],[13,5,14,5],[13,6,14,7],[13,8,14,8],[13,9,14,9],[15,2,16,2],[15,3,16,4],[15,5,16,5],[15,6,16,7],[15,8,16,8],[15,9,16,9],[17,2,18,2],[17,3,18,4],[17,5,18,5],[17,6,18,7],[17,8,18,8],[17,9,18,9],[19,2,20,2],[19,3,20,4],[19,5,20,5],[19,6,20,7],[19,8,20,8],[19,9,20,9],[21,2,22,2],[21,3,22,4],[21,5,22,5],[21,6,22,7],[21,8,22,8],[21,9,22,9],[24,0,25,9],[26,0,26,4],[26,6,26,9],[27,0,28,4],[27,5,28,5],[27,6,28,9],[29,0,30,4],[29,5,30,5],[29,6,30,9],[31,0,32,4],[31,5,32,5],[31,6,32,9],[34,0,35,9],[36,0,40,1],[36,3,36,5],[36,6,36,8],[37,3,37,5],[37,6,37,8],[38,3,38,5],[38,6,38,8],[39,3,39,5],[39,6,39,8],[40,3,40,5],[40,6,40,8],[42,0,63,1],[42,2,43,4],[42,5,43,7],[42,8,43,9],[44,2,52,4],[44,5,52,7],[44,8,44,9],[45,8,46,9],[47,8,47,9],[48,8,49,9],[50,8,50,9],[51,8,52,9],[53,2,54,4],[53,5,54,7],[53,8,54,9],[55,2,63,4],[55,5,63,7],[55,8,55,9],[56,8,58,9],[59,8,59,9],[60,8,63,9],[64,0,66,1],[64,2,66,9],[68,0,69,9],[70,0,70,4],[70,6,70,9],[71,0,72,4],[71,5,72,5],[71,6,72,9],[73,0,74,4],[73,5,74,5],[73,6,74,9],[76,0,91,1],[76,2,91,9]],"flags":["formulas_cached_only"]}
["o","사이트 정보"]
[]
["일반",null,"사이트 정보",null,"뉴프라임",null,"실 사 일",null,"2026-07-12"]
[]
[null,null,"주소",null,"경북 성주군 성주읍 성주산업단지로4길 28-29"]
[]
[null,null,"구분",null,"생산시설",null,"유형"]
[]
[null,null,"목적",null,"성주 뉴프라임 데이터 수집시스템 개발을 위한 NILM 설치 환경 조사"]
[]
[]
["참석인원",null,"Sl. No.","큐센텍",null,null,"이즈파크",null,null,"비고"]
[{"$nulls":3},"이름",null,"사인","이름",null,"사인"]
[null,null,1,"황혁순"]
[]
[null,null,2]
[]
[null,null,3]
[]
[null,null,4]
[]
[null,null,5]
[]
[]
[" - 요구조건"]
[]
["요구항목",{"$nulls":4},"확인","비고"]
["□  3상3선식 / 3상4선식 여부 확인",{"$nulls":4},"√","3상3선"]
[]
["□  220VAC 수용여부",{"$nulls":4},"√","220V 변환트랜스 확인  (콘센트별도설치필요)"]
[]
["□ NILM 설치 공간 확인",{"$nulls":4},"√","백판넬 및 C채널 가공 필요(난이도 中)"]
[]
[]
[" - 실사요소"]
[]
["분전반",null,"넘버","항목",null,null,"결과",null,null,"비고"]
[null,null,1,"메인 MCCB 용량",null,null,"슈나이더/ NSC630K / 3P",null,null,"630A"]
[null,null,2,"220V 콘센트 (or 트랜스) 유무",null,null,"변환트랜스",null,null,"콘센트공사"]
[null,null,3,"NILM 설치공간확인",null,null,"벽부 공간 활용 (백판넬 필요)"]
[null,null,4,"LoRa G/W 유선 LAN 포설",null,null,"지정된 위치에 1포트"]
[]
["구역정보",null,"1라인 NSC 630K",null,null,"1라인 변환트랜스",null,null,"위치"]
[]
[{"$nulls":8},"건물"]
[{"$nulls":8},"주1A동"]
[]
[{"$nulls":8},"층"]
[{"$nulls":8},1]
[]
[{"$nulls":8},"공정넘버"]
[{"$nulls":8},"제사공정"]
[]
[null,null,"2라인 NSC 630K",null,null,"2라인 변환트랜스",null,null,"관리자"]
[]
[{"$nulls":8},"이름"]
[{"$nulls":8},"뉴프라임\n김지호 과장"]
[]
[]
[{"$nulls":8},"연락처"]
[{"$nulls":8},"010-5277-7735"]
[]
[]
[]
["비고",null,"   220V 노출 콘센트 공사 필요, 벽면 사이드 판넬 추가설치 작업 필요"]
[]
[]
[]
[" - 의견"]
[]
["조율사항",{"$nulls":4},"확인","비고"]
["□ LoRa 안테나 설치를 위한 분전반 함체 천공작업 가능여부"]
[]
["□ 220V 디바이스 사용을 위한 추가공사 가능 여부"]
[]
[]
["레이아웃"]

{"sheet":"주2B동","index":2,"n_rows":77,"n_cols":10,"rows_kept":77,"merged":[[0,0,1,0],[0,1,1,9],[2,0,10,1],[2,2,3,3],[2,4,3,5],[2,6,3,7],[2,8,3,9],[4,2,5,3],[4,4,5,9],[6,2,7,3],[6,4,7,5],[6,6,7,7],[6,8,7,9],[8,2,10,3],[8,4,10,9],[11,0,22,1],[11,2,12,2],[11,3,11,5],[11,6,11,8],[11,9,12,9],[12,3,12,4],[12,6,12,7],[13,2,14,2],[13,3,14,4],[13,5,14,5],[13,6,14,7],[13,8,14,8],[13,9,14,9],[15,2,16,2],[15,3,16,4],[15,5,16,5],[15,6,16,7],[15,8,16,8],[15,9,16,9],[17,2,18,2],[17,3,18,4],[17,5,18,5],[17,6,18,7],[17,8,18,8],[17,9,18,9],[19,2,20,2],[19,3,20,4],[19,5,20,5],[19,6,20,7],[19,8,20,8],[19,9,20,9],[21,2,22,2],[21,3,22,4],[21,5,22,5],[21,6,22,7],[21,8,22,8],[21,9,22,9],[24,0,25,9],[26,0,26,4],[26,6,26,9],[27,0,28,4],[27,5,28,5],[27,6,28,9],[29,0,30,4],[29,5,30,5],[29,6,30,9],[31,0,32,4],[31,5,32,5],[31,6,32,9],[34,0,35,9],[36,0,40,1],[36,3,36,5],[36,6,36,8],[37,3,37,5],[37,6,37,8],[38,3,38,5],[38,6,38,8],[39,3,39,5],[39,6,39,8],[40,3,40,5],[40,6,40,8],[42,0,63,1],[42,2,43,4],[42,5,43,7],[42,8,43,9],[44,2,52,4],[44,5,52,7],[44,8,44,9],[45,8,46,9],[47,8,47,9],[48,8,49,9],[50,8,50,9],[51,8,52,9],[53,2,54,4],[53,5,54,7],[53,8,54,9],[55,2,63,4],[55,5,63,7],[55,8,55,9],[56,8,58,9],[59,8,59,9],[60,8,63,9],[64,0,66,1],[64,2,66,9],[68,0,69,9],[70,0,70,4],[70,6,70,9],[71,0,72,4],[71,5,72,5],[71,6,72,9],[73,0,74,4],[73,5,74,5],[73,6,74,9],[76,0,91,1],[76,2,91,9]],"flags":["formulas_cached_only"]}
["o","사이트 정보"]
[]
["일반",null,"사이트 정보",null,"뉴프라임",null,"실 사 일",null,"2026-07-12"]
[]
[null,null,"주소",null,"경북 성주군 성주읍 성주산업단지로4길 28-29"]
[]
[null,null,"구분",null,"생산시설",null,"유형"]
[]
[null,null,"목적",null,"성주 뉴프라임 데이터 수집시스템 개발을 위한 NILM 설치 환경 조사"]
[]
[]
["참석인원",null,"Sl. No.","큐센텍",null,null,"이즈파크",null,null,"비고"]
[{"$nulls":3},"이름",null,"사인","이름",null,"사인"]
[null,null,1,"황혁순"]
[]
[null,null,2]
[]
[null,null,3]
[]
[null,null,4]
[]
[null,null,5]
[]
[]
[" - 요구조건"]
[]
["요구항목",{"$nulls":4},"확인","비고"]
["□  3상3선식 / 3상4선식 여부 확인",{"$nulls":4},"√","3상3선"]
[]
["□  220VAC 수용여부",{"$nulls":4},"√","220V 콘센트있음"]
[]
["□ NILM 설치 공간 확인",{"$nulls":4},"√","왼쪽 콘센트 판넬 이용(난이도 下)"]
[]
[]
[" - 실사요소"]
[]
["분전반",null,"넘버","항목",null,null,"결과",null,null,"비고"]
[null,null,1,"메인 MCCB 용량",null,null,"비츠로/ VBE 54 / 3P",null,null,"50A"]
[null,null,2,"220V 콘센트 (or 트랜스) 유무",null,null,"220V 노출 콘센트"]
[null,null,3,"NILM 설치공간확인",null,null,"사이드 공간 활용 "]
[null,null,4,"LoRa G/W 유선 LAN 포설",null,null,"지정된 위치에 1포트"]
[]
["구역정보",null,"메인 분전반",null,null,"분기 MCCB",null,null,"위치"]
[]
[{"$nulls":8},"건물"]
[{"$nulls":8},"주2B동"]
[]
[{"$nulls":8},"층"]
[{"$nulls":8},1]
[]
[{"$nulls":8},"공정넘버"]
[{"$nulls":8},"제직공정"]
[]
[null,null,"제직기별 분전함 ",null,null,"220V 노출콘센트",null,null,"관리자"]
[]
[{"$nulls":8},"이름"]
[{"$nulls":8},"뉴프라임\n김지호 과장"]
[]
[]
[{"$nulls":8},"연락처"]
[{"$nulls":8},"010-5277-7735"]
[]
[]
[]
["비고",null,"   220V 노출 콘센트 위치변경후 사이드 판넬 이용 NILM 설치 가능  \n  총 23SET로 수량이 많아 충분한 공사일정을 계획해야 함 (3-4일 예상)"]
[]
[]
[]
[" - 의견"]
[]
["조율사항",{"$nulls":4},"확인","비고"]
["□ LoRa 안테나 설치를 위한 분전반 함체 천공작업 가능여부"]
[]
["□ 220V 디바이스 사용을 위한 추가공사 가능 여부"]
[]
[]
["레이아웃"]

{"sheet":"주3C동 ","index":3,"n_rows":77,"n_cols":10,"rows_kept":77,"merged":[[0,0,1,0],[0,1,1,9],[2,0,10,1],[2,2,3,3],[2,4,3,5],[2,6,3,7],[2,8,3,9],[4,2,5,3],[4,4,5,9],[6,2,7,3],[6,4,7,5],[6,6,7,7],[6,8,7,9],[8,2,10,3],[8,4,10,9],[11,0,22,1],[11,2,12,2],[11,3,11,5],[11,6,11,8],[11,9,12,9],[12,3,12,4],[12,6,12,7],[13,2,14,2],[13,3,14,4],[13,5,14,5],[13,6,14,7],[13,8,14,8],[13,9,14,9],[15,2,16,2],[15,3,16,4],[15,5,16,5],[15,6,16,7],[15,8,16,8],[15,9,16,9],[17,2,18,2],[17,3,18,4],[17,5,18,5],[17,6,18,7],[17,8,18,8],[17,9,18,9],[19,2,20,2],[19,3,20,4],[19,5,20,5],[19,6,20,7],[19,8,20,8],[19,9,20,9],[21,2,22,2],[21,3,22,4],[21,5,22,5],[21,6,22,7],[21,8,22,8],[21,9,22,9],[24,0,25,9],[26,0,26,4],[26,6,26,9],[27,0,28,4],[27,5,28,5],[27,6,28,9],[29,0,30,4],[29,5,30,5],[29,6,30,9],[31,0,32,4],[31,5,32,5],[31,6,32,9],[34,0,35,9],[36,0,40,1],[36,3,36,5],[36,6,36,8],[37,3,37,5],[37,6,37,8],[38,3,38,5],[38,6,38,8],[39,3,39,5],[39,6,39,8],[40,3,40,5],[40,6,40,8],[42,0,63,1],[42,2,43,4],[42,5,43,7],[42,8,43,9],[44,2,52,4],[44,5,52,7],[44,8,44,9],[45,8,46,9],[47,8,47,9],[48,8,49,9],[50,8,50,9],[51,8,52,9],[53,2,54,4],[53,5,54,7],[53,8,54,9],[55,2,63,4],[55,5,63,7],[55,8,55,9],[56,8,58,9],[59,8,59,9],[60,8,63,9],[64,0,66,1],[64,2,66,9],[68,0,69,9],[70,0,70,4],[70,6,70,9],[71,0,72,4],[71,5,72,5],[71,6,72,9],[73,0,74,4],[73,5,74,5],[73,6,74,9],[76,0,91,1],[76,2,91,9]],"flags":["formulas_cached_only"]}
["o","사이트 정보"]
[]
["일반",null,"사이트 정보",null,"뉴프라임",null,"실 사 일",null,"2026-07-12"]
[]
[null,null,"주소",null,"경북 성주군 성주읍 성주산업단지로4길 28-29"]
[]
[null,null,"구분",null,"생산시설",null,"유형"]
[]
[null,null,"목적",null,"성주 뉴프라임 데이터 수집시스템 개발을 위한 NILM 설치 환경 조사"]
[]
[]
["참석인원",null,"Sl. No.","큐센텍",null,null,"이즈파크",null,null,"비고"]
[{"$nulls":3},"이름",null,"사인","이름",null,"사인"]
[null,null,1,"황혁순"]
[]
[null,null,2]
[]
[null,null,3]
[]
[null,null,4]
[]
[null,null,5]
[]
[]
[" - 요구조건"]
[]
["요구항목",{"$nulls":4},"확인","비고"]
["□  3상3선식 / 3상4선식 여부 확인",{"$nulls":4},"√","3상4선"]
[]
["□  220VAC 수용여부",{"$nulls":4},"√","220V ELB (콘센트별도설치필요)"]
[]
["□ NILM 설치 공간 확인",{"$nulls":4},"√","설치공간 없음 (난이도 上)"]
[]
[]
[" - 실사요소"]
[]
["분전반",null,"넘버","항목",null,null,"결과",null,null,"비고"]
[null,null,1,"메인 MCCB 용량 (1라인)",null,null,"비츠로 / VBE 804 / 4P",null,null,"800A"]
[null,null,2,"메인 MCCB 용량 (2라인)",null,null,"제일전기 / CK800-C / 3P",null,null,"800A"]
[null,null,3,"220V 콘센트 (or 트랜스) 유무",null,null,"220V ELB",null,null,"콘센트공사"]
[null,null,4,"NILM 설치공간확인",null,null,"공간 협의 필요",null,null,"특고압 위험"]
[]
["구역정보",null,"1라인 분전반 ",null,null,"1라인 MCCB / 800A",null,null,"위치"]
[]
[{"$nulls":8},"건물"]
[{"$nulls":8},"주3C동"]
[]
[{"$nulls":8},"층"]
[{"$nulls":8},1]
[]
[{"$nulls":8},"공정넘버"]
[{"$nulls":8},"코팅공정"]
[]
[null,null,"2라인 분전함 ",null,null,"2라인 CK800-C / 800A",null,null,"관리자"]
[]
[{"$nulls":8},"이름"]
[{"$nulls":8},"뉴프라임\n김지호 과장"]
[]
[]
[{"$nulls":8},"연락처"]
[{"$nulls":8},"010-5277-7735"]
[]
[]
[]
["비고",null,"   220V 인입이 매우 어렵고 특고압으로 작업 난이도 높음 (고온습한환경 및 유해화학물 주의)\n   NILM 설치공간이 없어 설치시 협의 필요함"]
[]
[]
[]
[" - 의견"]
[]
["조율사항",{"$nulls":4},"확인","비고"]
["□ LoRa 안테나 설치를 위한 분전반 함체 천공작업 가능여부"]
[]
["□ 220V 디바이스 사용을 위한 추가공사 가능 여부"]
[]
[]
["레이아웃"]

{"sheet":"주5동(1~2라인)","index":4,"n_rows":77,"n_cols":10,"rows_kept":77,"merged":[[0,0,1,0],[0,1,1,9],[2,0,10,1],[2,2,3,3],[2,4,3,5],[2,6,3,7],[2,8,3,9],[4,2,5,3],[4,4,5,9],[6,2,7,3],[6,4,7,5],[6,6,7,7],[6,8,7,9],[8,2,10,3],[8,4,10,9],[11,0,22,1],[11,2,12,2],[11,3,11,5],[11,6,11,8],[11,9,12,9],[12,3,12,4],[12,6,12,7],[13,2,14,2],[13,3,14,4],[13,5,14,5],[13,6,14,7],[13,8,14,8],[13,9,14,9],[15,2,16,2],[15,3,16,4],[15,5,16,5],[15,6,16,7],[15,8,16,8],[15,9,16,9],[17,2,18,2],[17,3,18,4],[17,5,18,5],[17,6,18,7],[17,8,18,8],[17,9,18,9],[19,2,20,2],[19,3,20,4],[19,5,20,5],[19,6,20,7],[19,8,20,8],[19,9,20,9],[21,2,22,2],[21,3,22,4],[21,5,22,5],[21,6,22,7],[21,8,22,8],[21,9,22,9],[24,0,25,9],[26,0,26,4],[26,6,26,9],[27,0,28,4],[27,5,28,5],[27,6,28,9],[29,0,30,4],[29,5,30,5],[29,6,30,9],[31,0,32,4],[31,5,32,5],[31,6,32,9],[34,0,35,9],[36,0,40,1],[36,3,36,5],[36,6,36,8],[37,3,37,5],[37,6,37,8],[38,3,38,5],[38,6,38,8],[39,3,39,5],[39,6,39,8],[40,3,40,5],[40,6,40,8],[42,0,63,1],[42,2,43,4],[42,5,43,7],[42,8,43,9],[44,2,52,4],[44,5,52,7],[44,8,44,9],[45,8,46,9],[47,8,47,9],[48,8,49,9],[50,8,50,9],[51,8,52,9],[53,2,54,4],[53,5,54,7],[53,8,54,9],[55,2,63,4],[55,5,63,7],[55,8,55,9],[56,8,58,9],[59,8,59,9],[60,8,63,9],[64,0,66,1],[64,2,66,9],[68,0,69,9],[70,0,70,4],[70,6,70,9],[71,0,72,4],[71,5,72,5],[71,6,72,9],[73,0,74,4],[73,5,74,5],[73,6,74,9],[76,0,91,1],[76,2,91,9]],"flags":["formulas_cached_only"]}
["o","사이트 정보"]
[]
["일반",null,"사이트 정보",null,"뉴프라임",null,"실 사 일",null,"2026-07-12"]
[]
[null,null,"주소",null,"경북 성주군 성주읍 성주산업단지로4길 28-29"]
[]
[null,null,"구분",null,"생산시설",null,"유형"]
[]
[null,null,"목적",null,"성주 뉴프라임 데이터 수집시스템 개발을 위한 NILM 설치 환경 조사"]
[]
[]
["참석인원",null,"Sl. No.","큐센텍",null,null,"이즈파크",null,null,"비고"]
[{"$nulls":3},"이름",null,"사인","이름",null,"사인"]
[null,null,1,"황혁순"]
[]
[null,null,2]
[]
[null,null,3]
[]
[null,null,4]
[]
[null,null,5]
[]
[]
[" - 요구조건"]
[]
["요구항목",{"$nulls":4},"확인","비고"]
["□  3상3선식 / 3상4선식 여부 확인",{"$nulls":4},"√","3상4선"]
[]
["□  220VAC 수용여부",{"$nulls":4},"√","220V 콘센트 있음"]
[]
["□ NILM 설치 공간 확인",{"$nulls":4},"√","설치공간 협의 (난이도 下)"]
[]
[]
[" - 실사요소"]
[]
["분전반",null,"넘버","항목",null,null,"결과",null,null,"비고"]
[null,null,1,"메인 MCCB 용량 (1라인)",null,null,"LS / ABS 404c / 4P",null,null,"400A"]
[null,null,2,"메인 MCCB 용량 (2라인)",null,null,"LS / ABS 404c / 4P",null,null,"400A"]
[null,null,3,"220V 콘센트 (or 트랜스) 유무",null,null,"220V 콘센트"]
[null,null,4,"NILM 설치공간확인",null,null,"공간 협의 필요",null,null,"특고압 주의"]
[]
["구역정보",null,"1라인 MCCB",null,null,"1라인 CT센서(WYCR-40)",null,null,"위치"]
[]
[{"$nulls":8},"건물"]
[{"$nulls":8},"주5동"]
[]
[{"$nulls":8},"층"]
[{"$nulls":8},1]
[]
[{"$nulls":8},"공정넘버"]
[{"$nulls":8},"합지공정"]
[]
[null,null,"2라인 MCCB",null,null,"2라인 CT센서(WYCR-40)",null,null,"관리자"]
[]
[{"$nulls":8},"이름"]
[{"$nulls":8},"뉴프라임\n김지호 과장"]
[]
[]
[{"$nulls":8},"연락처"]
[{"$nulls":8},"010-5277-7735"]
[]
[]
[]
["비고",null,"  NILM (특고압 주의) 설치공간 협의"]
[]
[]
[]
[" - 의견"]
[]
["조율사항",{"$nulls":4},"확인","비고"]
["□ LoRa 안테나 설치를 위한 분전반 함체 천공작업 가능여부"]
[]
["□ 220V 디바이스 사용을 위한 추가공사 가능 여부"]
[]
[]
["레이아웃"]

{"sheet":"주5동(3~4라인)","index":5,"n_rows":77,"n_cols":10,"rows_kept":77,"merged":[[0,0,1,0],[0,1,1,9],[2,0,10,1],[2,2,3,3],[2,4,3,5],[2,6,3,7],[2,8,3,9],[4,2,5,3],[4,4,5,9],[6,2,7,3],[6,4,7,5],[6,6,7,7],[6,8,7,9],[8,2,10,3],[8,4,10,9],[11,0,22,1],[11,2,12,2],[11,3,11,5],[11,6,11,8],[11,9,12,9],[12,3,12,4],[12,6,12,7],[13,2,14,2],[13,3,14,4],[13,5,14,5],[13,6,14,7],[13,8,14,8],[13,9,14,9],[15,2,16,2],[15,3,16,4],[15,5,16,5],[15,6,16,7],[15,8,16,8],[15,9,16,9],[17,2,18,2],[17,3,18,4],[17,5,18,5],[17,6,18,7],[17,8,18,8],[17,9,18,9],[19,2,20,2],[19,3,20,4],[19,5,20,5],[19,6,20,7],[19,8,20,8],[19,9,20,9],[21,2,22,2],[21,3,22,4],[21,5,22,5],[21,6,22,7],[21,8,22,8],[21,9,22,9],[24,0,25,9],[26,0,26,4],[26,6,26,9],[27,0,28,4],[27,5,28,5],[27,6,28,9],[29,0,30,4],[29,5,30,5],[29,6,30,9],[31,0,32,4],[31,5,32,5],[31,6,32,9],[34,0,35,9],[36,0,40,1],[36,3,36,5],[36,6,36,8],[37,3,37,5],[37,6,37,8],[38,3,38,5],[38,6,38,8],[39,3,39,5],[39,6,39,8],[40,3,40,5],[40,6,40,8],[42,0,63,1],[42,2,43,4],[42,5,43,7],[42,8,43,9],[44,2,52,4],[44,5,52,7],[44,8,44,9],[45,8,46,9],[47,8,47,9],[48,8,49,9],[50,8,50,9],[51,8,52,9],[53,2,54,4],[53,5,54,7],[53,8,54,9],[55,2,63,4],[55,5,63,7],[55,8,55,9],[56,8,58,9],[59,8,59,9],[60,8,63,9],[64,0,66,1],[64,2,66,9],[68,0,69,9],[70,0,70,4],[70,6,70,9],[71,0,72,4],[71,5,72,5],[71,6,72,9],[73,0,74,4],[73,5,74,5],[73,6,74,9],[76,0,91,1],[76,2,91,9]],"flags":["formulas_cached_only"]}
["o","사이트 정보"]
[]
["일반",null,"사이트 정보",null,"뉴프라임",null,"실 사 일",null,"2026-07-12"]
[]
[null,null,"주소",null,"경북 성주군 성주읍 성주산업단지로4길 28-29"]
[]
[null,null,"구분",null,"생산시설",null,"유형"]
[]
[null,null,"목적",null,"성주 뉴프라임 데이터 수집시스템 개발을 위한 NILM 설치 환경 조사"]
[]
[]
["참석인원",null,"Sl. No.","큐센텍",null,null,"이즈파크",null,null,"비고"]
[{"$nulls":3},"이름",null,"사인","이름",null,"사인"]
[null,null,1,"황혁순"]
[]
[null,null,2]
[]
[null,null,3]
[]
[null,null,4]
[]
[null,null,5]
[]
[]
[" - 요구조건"]
[]
["요구항목",{"$nulls":4},"확인","비고"]
["□  3상3선식 / 3상4선식 여부 확인",{"$nulls":4},"√","3상4선"]
[]
["□  220VAC 수용여부",{"$nulls":4},"√","220V ELB (콘센트별도설치필요)"]
[]
["□ NILM 설치 공간 확인",{"$nulls":4},"√","설치공간 협의 (난이도 中)"]
[]
[]
[" - 실사요소"]
[]
["분전반",null,"넘버","항목",null,null,"결과",null,null,"비고"]
[null,null,1,"메인 MCCB 용량 (3라인)",null,null,"LS / ABS 204c / 4P",null,null,"200A"]
[null,null,2,"메인 MCCB 용량 (4라인)",null,null,"LS / SB-204S / 4P",null,null,"125A"]
[null,null,3,"220V 콘센트 (or 트랜스) 유무",null,null,"220V ELB",null,null,"콘센트공사"]
[null,null,4,"NILM 설치공간확인",null,null,"공간 협의 필요",null,null,"특고압 주의"]
[]
["구역정보",null,"3라인 MCCB",null,null,"3라인 CT센서(KBJ-25)",null,null,"위치"]
[]
[{"$nulls":8},"건물"]
[{"$nulls":8},"주5동"]
[]
[{"$nulls":8},"층"]
[{"$nulls":8},1]
[]
[{"$nulls":8},"공정넘버"]
[{"$nulls":8},"합지공정"]
[]
[null,null,"4라인 분전반",null,null,"사진",null,null,"관리자"]
[]
[{"$nulls":8},"이름"]
[{"$nulls":8},"뉴프라임\n김지호 과장"]
[]
[]
[{"$nulls":8},"연락처"]
[{"$nulls":8},"010-5277-7735"]
[]
[]
[]
["비고",null," 3라인 NILM (특고압 주의) 설치공간 있으나 4라인 분전함 NILM 설치공간 없음   "]
[]
[]
[]
[" - 의견"]
[]
["조율사항",{"$nulls":4},"확인","비고"]
["□ LoRa 안테나 설치를 위한 분전반 함체 천공작업 가능여부"]
[]
["□ 220V 디바이스 사용을 위한 추가공사 가능 여부"]
[]
[]
["레이아웃"]

{"sheet":"주7동","index":6,"n_rows":77,"n_cols":10,"rows_kept":77,"merged":[[0,0,1,0],[0,1,1,9],[2,0,10,1],[2,2,3,3],[2,4,3,5],[2,6,3,7],[2,8,3,9],[4,2,5,3],[4,4,5,9],[6,2,7,3],[6,4,7,5],[6,6,7,7],[6,8,7,9],[8,2,10,3],[8,4,10,9],[11,0,22,1],[11,2,12,2],[11,3,11,5],[11,6,11,8],[11,9,12,9],[12,3,12,4],[12,6,12,7],[13,2,14,2],[13,3,14,4],[13,5,14,5],[13,6,14,7],[13,8,14,8],[13,9,14,9],[15,2,16,2],[15,3,16,4],[15,5,16,5],[15,6,16,7],[15,8,16,8],[15,9,16,9],[17,2,18,2],[17,3,18,4],[17,5,18,5],[17,6,18,7],[17,8,18,8],[17,9,18,9],[19,2,20,2],[19,3,20,4],[19,5,20,5],[19,6,20,7],[19,8,20,8],[19,9,20,9],[21,2,22,2],[21,3,22,4],[21,5,22,5],[21,6,22,7],[21,8,22,8],[21,9,22,9],[24,0,25,9],[26,0,26,4],[26,6,26,9],[27,0,28,4],[27,5,28,5],[27,6,28,9],[29,0,30,4],[29,5,30,5],[29,6,30,9],[31,0,32,4],[31,5,32,5],[31,6,32,9],[34,0,35,9],[36,0,40,1],[36,3,36,5],[36,6,36,8],[37,3,37,5],[37,6,37,8],[38,3,38,5],[38,6,38,8],[39,3,39,5],[39,6,39,8],[40,3,40,5],[40,6,40,8],[42,0,63,1],[42,2,43,4],[42,5,43,7],[42,8,43,9],[44,2,52,4],[44,5,52,7],[44,8,44,9],[45,8,46,9],[47,8,47,9],[48,8,49,9],[50,8,50,9],[51,8,52,9],[53,2,54,4],[53,5,54,7],[53,8,54,9],[55,2,63,4],[55,5,63,7],[55,8,55,9],[56,8,58,9],[59,8,59,9],[60,8,63,9],[64,0,66,1],[64,2,66,9],[68,0,69,9],[70,0,70,4],[70,6,70,9],[71,0,72,4],[71,5,72,5],[71,6,72,9],[73,0,74,4],[73,5,74,5],[73,6,74,9],[76,0,91,1],[76,2,91,9]],"flags":["formulas_cached_only"]}
["o","사이트 정보"]
[]
["일반",null,"사이트 정보",null,"뉴프라임",null,"실 사 일",null,"2026-07-12"]
[]
[null,null,"주소",null,"경북 성주군 성주읍 성주산업단지로4길 28-29"]
[]
[null,null,"구분",null,"생산시설",null,"유형"]
[]
[null,null,"목적",null,"성주 뉴프라임 데이터 수집시스템 개발을 위한 NILM 설치 환경 조사"]
[]
[]
["참석인원",null,"Sl. No.","큐센텍",null,null,"이즈파크",null,null,"비고"]
[{"$nulls":3},"이름",null,"사인","이름",null,"사인"]
[null,null,1,"황혁순"]
[]
[null,null,2]
[]
[null,null,3]
[]
[null,null,4]
[]
[null,null,5]
[]
[]
[" - 요구조건"]
[]
["요구항목",{"$nulls":4},"확인","비고"]
["□  3상3선식 / 3상4선식 여부 확인",{"$nulls":4},"√","3상3선"]
[]
["□  220VAC 수용여부",{"$nulls":4},"√","220V ELB (콘센트별도설치필요)"]
[]
["□ NILM 설치 공간 확인",{"$nulls":4},"√","설치공간 협소 (난이도 上)"]
[]
[]
[" - 실사요소"]
[]
["분전반",null,"넘버","항목",null,null,"결과",null,null,"비고"]
[null,null,1,"메인 MCCB 용량 (1라인)",null,null,"LS / ABS 53c / 3P",null,null,"50A"]
[null,null,2,"메인 MCCB 용량 (2라인)",null,null,"LS / ABE 203 / 3P",null,null,"225A"]
[null,null,3,"메인 MCCB 용량 (3라인)",null,null,"LS / ABE-33b / 3P",null,null,"30A"]
[null,null,4,"220V 콘센트 (or 트랜스) 유무",null,null,"220V ELB",null,null,"콘센트공사"]
[]
["구역정보",null,"1라인 ABS 53c",null,null,"2라인 ABE203",null,null,"위치"]
[]
[{"$nulls":8},"건물"]
[{"$nulls":8},"주7동"]
[]
[{"$nulls":8},"층"]
[{"$nulls":8},1]
[]
[{"$nulls":8},"공정넘버"]
[{"$nulls":8},"코로나 천공 공정"]
[]
[null,null,"3라인 ABE 33b",null,null,"3라인 220V ELB",null,null,"관리자"]
[]
[{"$nulls":8},"이름"]
[{"$nulls":8},"뉴프라임\n김지호 과장"]
[]
[]
[{"$nulls":8},"연락처"]
[{"$nulls":8},"010-5277-7735"]
[]
[]
[]
["비고",null," 3라인 NILM (특고압 주의) 설치공간 있으나 4라인 분전함 NILM 설치공간 없음   "]
[]
[]
[]
[" - 의견"]
[]
["조율사항",{"$nulls":4},"확인","비고"]
["□ LoRa 안테나 설치를 위한 분전반 함체 천공작업 가능여부"]
[]
["□ 220V 디바이스 사용을 위한 추가공사 가능 여부"]
[]
[]
["레이아웃"]